## Instructions
Instructions for using the "bh_sizing" worksheet, v. 1
1) Fill in the coloured cells (D3 to D21 or E3 to E21) of the section "1st set of inputs" with your input parameters | Single borehole design | Multiple boreholes design
2) The results of the calculations with Tp = 0 (without taking into account the thermal interference among boreholes) are given in section "1st set of results". For single borehole designs, calculations stop here and the value in cell D35 is the required borehole depth. For multiple boreholes, the length given in cell D35 should be regarded as a first approximation of the total borehole length.
3) To size a borefield by taking into account the thermal interference, determine the three parameters B (borehole spacing) , NB (number of boreholes) and A (borefield aspect ratio). Use the 1st set of results, which gives a first approximation of the final value of the borehole length, to estimate these three parameters.
4) Fill in the coloured cells (E38, E39, E40) of the section "2nd set of inputs" with the values of B, NB, and A.
5) The final results are given at the end of the section "final results", i.e, cells E69 and E70.
ASHRAE does not warrant nor guarantee the spreadsheet “Borehole Sizing." The entire risk of the use of any information contained herein is assumed by the user

## bh_sizing
1st SET OF INPUTS |  | UNITS | Single borehole | Multiple boreholes
Ground loads
peak hourly ground load | qh | W | 12000 | -392250 | Sign convention: +: heat injection to the ground -: heat extraction from the ground
monthly ground load | qm | W | 6000 | -100000
yearly average ground load | qy | W | 1500 | -1762
Ground properties
thermal conductivity | k | W.m-1K-1 | 2 | 2.25
thermal diffusivity | α | m2.day-1 | 0.086 | 0.06757 | <- Warning: α must be in the range between 0.025 and 0.2 m²/day
Undisturbed ground temperature | Tg | °C | 15 | 12.41
Fluid properties
thermal heat capacity | Cp | J.kg-1.K-1 | 4200 | 4000
total mass flow rate per kW of peak hourly ground load | mfls | kg.s-1.kW-1 | 0.05 | 0.074 | <- Mass flow rate in kg/s divided by the absolute value of the peak hourly ground load in kW
max/min heat pump inlet temperature | TinHP | °C | 40.2 | 4.44 | <- Design criterion for the operation of the heat pump
Borehole characteristics
borehole radius | rbore | m | 0.06 | 0.054 | <- Warning: rbore must be in the range between 0.05 and 0.1 m
pipe inner radius | rpin | m | 0.01365 | 0.01365
pipe outer radius | rpext | m | 0.0167 | 0.0167
grout thermal conductivity | kgrout | W.m-1.K-1 | 1.5 | 1.73
pipe thermal conductivity | kpipe | W.m-1.K-1 | 0.42 | 0.45
center-to-center distance between pipes | LU | m | 0.0511 | 0.0471
internal convection coefficient | hconv | W.m-2.K-1 | 1000 | 1000
1st SET OF RESULTS
Calculation of the effective borehole thermal resistance
convective resistance | Rconv | m.K.W-1 | 0.01166 | 0.01166
pipe resistance | Rp | m.K.W-1 | 0.076421 | 0.071326
grout resistance | Rg | m.K.W-1 | 0.076114 | 0.06005
effective borehole thermal resistance | Rb | m.K.W-1 | 0.12015 | 0.10154
Calculation of the effective ground thermal resistances
short term (6 hours pulse) | R6h | m.K.W-1 | 0.11446 | 0.10067
medium term (1 month pulse) | R1m | m.K.W-1 | 0.18021 | 0.16
long term (10 years pulse) | R10y | m.K.W-1 | 0.19084 | 0.16963
Total length calculation assuming no borehole thermal interference
heat pump outlet temperature | ToutHP | °C | 44.9619 | 1.0616
average fluid temperature in the borehole | Tm | °C | 42.581 | 2.7508
total length | L | m | 151.6573 | 9899.2563
2nd SET OF INPUTS
Borefield characteristics
distance between boreholes | B | m |  | 6.1
number of boreholes | NB | - |  | 120 | <- Warning: NB must be in the range between 4 and 144
borefield aspect ratio | A | - |  | 1.2 | <- Number of boreholes in the longest direction over the number of borehole in the other direction, A must be in the range between 1 and 9
FINAL RESULTS
Total length calculation (with Tp)
1st iteration
distance-depth ratio | B/H | - |  | 0.073945 | Important note on the evaluation of Tp:
logarithm of dimensionless time | ln(t10y/ts) | - |  | -1.1196 | The correlation for Tp is based on 1485 simulations covering the following range of borefield configurations:
temperature penalty | Tp | °C |  | -0.24003
total borefield length | L | m |  | 10151.5156
2nd iteration
distance-depth ratio | B/H | - |  | 0.072107
logarithm of dimensionless time | ln(t10y/ts) | - |  | -1.17
temperature penalty | Tp | °C |  | -0.23831
total borefield length | L | m |  | 10149.6679
3rd iteration |  |  |  |  | When used within these ranges, Tp is typically accurate to within +/- 10%.
distance-depth ratio | B/H | - |  | 0.072121 | However, in certain cases, when Tp is near zero, values of Tp are less accurate
logarithm of dimensionless time | ln(t10y/ts) | - |  | -1.1696 | This inaccuracy combined with small values of (Tm-Tg) can lead to inaccurate borehole depths
temperature penalty | Tp | °C |  | -0.23832
total borefield length | L | m |  | 10149.683
4th iteration
distance-depth ratio | B/H | - |  | 0.07212
logarithm of dimensionless time | ln(t10y/ts) | - |  | -1.1696
temperature penalty | Tp | °C |  | -0.23832
total borefield length | L | m |  | 10149.6829
5th iteration
distance-depth ratio | B/H | - |  | 0.07212
logarithm of dimensionless time | ln(t10y/ts) | - |  | -1.1696
temperature penalty | Tp | °C |  | -0.23832
total borefield length | L | m |  | 10149.6829
Final results
total borefield length | L | m |  | 10149.6829
borehole depth | H | m |  | 84.5807

## coefficients
Coefficients for f6h, f1m, f10y functions |  |  |  | Coefficients for Tp correlation
| f6h | f1m | f10y | Tp function's coefficients
a0 | 0.66194 | 0.41327 | 0.30576 | b0 | 7.8189
a1 | -4.8157 | 0.2913 | 0.089874 | b1 | -64.27
a2 | 15.0357 | 0.075893 | -0.091518 | b2 | 153.87
a3 | -0.098794 | 0.1564 | -0.038725 | b3 | -84.809
a4 | 0.029179 | -0.22894 | 0.16909 | b4 | 3.461
a5 | 0.11385 | -0.0049276 | -0.028817 | b5 | -0.94753
a6 | 0.0056109 | -0.002695 | -0.0028866 | b6 | -0.060416
a7 | 0.77963 | -0.63804 | -0.17232 | b7 | 1.5631
a8 | -0.32439 | 0.29508 | 0.03112 | b8 | -0.0089416
a9 | -0.018241 | 0.14933 | -0.11884 | b9 | 1.9061e-05
|  |  |  | b10 | -2.289
|  |  |  | b11 | 0.10187
|  |  |  | b12 | 0.006569
|  |  |  | b13 | -40.918
|  |  |  | b14 | 15.557
|  |  |  | b15 | -19.107
|  |  |  | b16 | 0.10529
|  |  |  | b17 | 25.501
|  |  |  | b18 | -2.1177
|  |  |  | b19 | 77.529
|  |  |  | b20 | -50.454
|  |  |  | b21 | 76.352
|  |  |  | b22 | -0.53719
|  |  |  | b23 | -132
|  |  |  | b24 | 12.878
|  |  |  | b25 | 0.12697
|  |  |  | b26 | -0.00040284
|  |  |  | b27 | -0.072065
|  |  |  | b28 | 0.00095184
|  |  |  | b29 | -0.024167
|  |  |  | b30 | 9.6811e-05
|  |  |  | b31 | 0.028317
|  |  |  | b32 | -0.0010905
|  |  |  | b33 | 0.12207
|  |  |  | b34 | -0.007105
|  |  |  | b35 | -0.0011129
|  |  |  | b36 | -0.00045566
Do not change or erase these tables